SECTION 08 90 00

LOUVERS AND VENTS

PART 1 - GENERAL

1.01	DESCRIPTION:   Division 1 applies to this Section.  Provide louvers and vents complete

as indicated, specified, and required.

A. 	Work In This Section:  Principal items include:

1. 	Extruded aluminum louvers.

2. 	Formed sheet metal louvers.

3. 	Formed sheet metal door louvers.

4. 	Gravity / dormer vents.

5. 	Prefabricated dryer vents and tubing.

B. 	Related Work Not In This Section:

1. 	Caulking and sealants.

2. 	Paint.

3. 	Air-handling louvers connected to ductwork.

4. 	Blank-off plates for air-handling louvers.

5. 	Louvers in hollow metal doors and frames.

6.	Vents as specified in other sections.

1.02 	QUALITY ASSURANCE:

A. 	Performance:  Where louvers are indicated to comply with specific performance

requirements, provide units whose performance ratings have been determined in

compliance with Air Movement and Control Association (AMCA) Standard 500.

B. 	AMCA Certification:  Where indicated, provide louvers with AMCA Certified

Ratings Seal evidencing that product complies with above requirements.

1. 	Comply with SMACNA "Architectural Sheet Metal Manual" recommendations for fabrication, construction details and installation

procedures, except as otherwise indicated.

C. 	Field Measurements:  Verify size, location and placement of louver units prior to

fabrication, wherever possible.

D. 	Shop Assembly:  Coordinate field measurements and shop drawings with

fabrication and shop assembly to minimize field adjustments, splicing,

mechanical joints and field assembly of units.   Preassemble units in shop to

greatest extent possible and disassemble as necessary for shipping and handling

limitations.  Clearly mark units for reassembly and coordinated installation.

1.03 	SUBMITTALS:  Refer to Section 01 33 00 for procedures.

A. 	Product Data:  If requested by Owner submit manufacturer’s specifications;

certified test data, where applicable; and installation instructions for required

products, including finishes.

B. 	Shop Drawings:  If requested by Owner and/or Architect submit shop drawings

for fabrication and erection of louver units and accessories.   Include plans,

elevations and details of sections and connections to adjoining work.   Indicate

materials, finishes, fasteners, joinery and other information to determine

compliance with specified requirements.

C. 	Samples:  Submit six-inch square of each required aluminum finish.  Prepare

samples on metal of the same gauge and alloy to be used in work.  Where

normal color and texture variations are to be expected, include two or more units

in each sample showing the limits of such variations.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS:

A. 	Available Manufacturers:  Subject to compliance with requirements,

manufacturers offering products which may be incorporated in the work include,

but are not limited to, the following:

Airline Products Company

The Airolite Company

American Warming and Ventilating Company

Construction Specialties, Inc.

Industrial Louvers, Inc.

Ruskin Manufacturing Company

2.02 	MATERIALS:

A. 	Galvanized Sheet Steel:  ASTM A526 and A527, with ASTM A525, G90 zinc

coating, mill phosphatized.

B. 	Cold-rolled Sheet Steel:  ASTM A366, Class 1, matte finish.

C. 	Aluminum Sheet:   ASTM B209, Alloy 3003 or 5005 with temper as required for

forming, or as otherwise recommended by metal producer to provide required

finish.

D. 	Aluminum Extrusions:  ASTM B221, Alloy 6063-T52.

E. 	Fastenings:  Use same material as items fastened, unless otherwise indicated.

Fasteners for exterior applications may be hot-dip galvanized, stainless steel or

aluminum.  Provide types, gauges and lengths to suit unit installation conditions.

Use Phillips flat-head machine screws for exposed fasteners, unless otherwise

indicated.

F. 	Anchors and Inserts:  Use non-ferrous metal or hot-dip galvanized anchors and

inserts for exterior installations and elsewhere as required for corrosion

resistance.  Use steel or lead expansion bolt devices for drilled-in-place anchors.

Furnish inserts, as required, to be set into concrete or masonry work.

G. 	Bituminous Paint:  SSPC-Paint 12 (cold-applied asphalt mastic).

2.03 	FABRICATION, GENERAL:

A. 	Provide louvers and accessories of design, materials, sizes, depth, arrangement,  and metal thicknesses indicated, or if not indicated, as required for optimum performance with respect to airflow; water penetration; air leakage, where  applicable (for adjustable units, if any); strength; durability; and uniform appearance.

B. 	Fabricate frames including integral sills to suit adjacent construction with tolerances for installation including application of sealants in joints between

louvers and adjoining work, where applicable.

C. 	Include supports, anchorages, and accessories required to achieve a complete

assembly.

D. 	Provide vertical mullions of type and at spacings indicated but not further apart

than recommended by manufacturer of seventy-two inch on center whichever is

less.  At horizontal joints between louver units provide horizontal mullions except

where continuous vertical assemblies are indicated.

E. 	Provide sill extensions and loose sills made of same material as louvers, where

indicated, or required for drainage to exterior and to prevent water penetrating to

interior.

F. 	Join frame members to one another and to stationary louver blades by welding,

except where indicated otherwise or where field bolted connections between

frame members are made necessary by size of louvers.   Maintain equal blade

spacing, including separation between blades and frames at head and sill, to

produce uniform appearance.

2.04 	STATIONARY FORMED SHEET METAL LOUVERS:

A. 	Horizontal Drainable Blade Louvers:  Unit designed to collect  and drain water

to exterior at sill by means of gutters on front edges of louver blades and channels in jambs and mullions; of depth  and sizes indicated, fabricated from the following metal:

1. 	Aluminum:  Not less than 14 gauge.

2.05 	ADJUSTABLE LOUVERS:

A. 	Operation:  Provide adjustable blade louvers (AdjLvr) at locations and of type

indicated; with manufacturer’s recommended bearings and operating

mechanisms to suit louver size and method of operation.

1. 	Hand operation with spring, chain, wall bracket, and 160 degree F (71

degrees C) fusible link.

2.06 	LOUVER SCREENS:  Provide removable screens for exterior louvers where indicated.

Fabricate screen frames of same metal and finish as louver units to which secured,

unless otherwise indicated.  Provide rewireable frames consisting of formed or extruded

metal with a driven spline or insert for securing screen mesh.  Use insect screen where

indicated, of the following:

1. Insect mesh, 0.063-inch aluminum wire.

A. 	Locate Screens on inside face of louvers, unless otherwise indicated.   Secure

screens to louver frames with machine screws, spaced at each corner and at

twelve inch on center between.

2.07 	PREFABRICATED DRYER VENTS:  Provide and install prefabricated dryer vents and tubing as manufactured by a manufacturer doing this type of business for at least 10 years. Coordinate with the rough carpenter for opening requirements and plumbing as to their requirements for proper installation of dryer vents where indicated on drawings.

2.08 	METAL FINISHES:  Comply with NAAMM "Metal Finishes Manual” for finish designations and application recommendations, except as otherwise indicated.  Apply finishes in factory after products are assembled.  Protect finishes on exposed surfaces with protective covering, prior to shipment.   Remove scratches and blemishes from exposed surfaces which will be visible after completing finishing process.  Provide colors or color matches as indicated, if not otherwise indicated, as selected by Architect from manufacturer's standard colors.

A. 	Ferrous Metal Finishes:

1. 	Preparation:  Clean surfaces of dirt, grease and loose rust or mill scale,

including items fabricated from galvanized steel, if any.  Apply finish to

surfaces of fabricated and assembled units, whether exposed or

concealed when installed, after pretreating with a conversion coating

suited to organic coating applied over it.

2. 	Factory-Primed Finish:  Where painting after installation is indicated (not

work of this section), apply air-dried primer immediately following cleaning

and pretreatment.

PART 3 - EXECUTION

3.01 	PREPARATION:  Coordinate setting drawings, diagrams, templates, instructions and

directions for installation of anchorages which are to be embedded in concrete or

masonry construction.  Coordinate delivery of such items to project site.

3.02 	INSTALLATION:  Locate and place louver units plumb, level and in proper alignment

with adjacent work.

A. 	Use Concealed Anchorages wherever possible.  Provide brass or lead washers

fitted to screws where required to protect metal surfaces and to make a weather-tight connection.

B. 	Form Tight Joints with exposed connections accurately fitted together.   Provide

reveals and openings for sealants and joint fillers, as indicated.

C. 	Repair Finishes damaged by cutting, welding, soldering and grinding operations

required for fitting and jointing.  Restore finishes so there is no evidence of

corrective work.  Return items which cannot be refinished in the field to shop,

make required alterations, and refinish entire unit, or provide new units, at

Contractor's option.

D. 	Protect galvanized and non-ferrous metal surfaces from corrosion of galvanic

action by application of a heavy coating of bituminous paint on surfaces which

will be in contact with concrete, masonry or dissimilar metals.

E. 	Provide concealed gaskets, flashings, joint fillers, and insulation, and install as

work progresses to make the installations weathertight.

F. 	Refer to Section 07 90 00 for sealants in connection with installation of louvers.

END OF SECTION