Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221429 - SUMP PUMPS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Terminology and descriptions for pumps used in this Section are from HI 1.1-1.2.

Submersible sump pumps.

Wet-pit-volute sump pumps.

Sump-pump basins and basin covers.

Packaged drainage-pump units.

Related Section:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 221329 "Sanitary Sewerage Pumps" for effluent and sewage pumps.

ACTION SUBMITTALS

Product Data:  For each type of product indicated.  [Include construction details, material descriptions, dimensions of individual components and profiles.] [Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.]

Wiring Diagrams:  For power, signal, and control wiring.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:  For pumps and controls, to include in operation and maintenance manuals.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

UL Compliance:  Comply with UL 778 for motor-operated water pumps.

DELIVERY, STORAGE, AND HANDLING

Retain shipping flange protective covers and protective coatings during storage.

Protect bearings and couplings against damage.

Comply with pump manufacturer's written rigging instructions for handling.

PRODUCTS

SUBMERSIBLE SUMP PUMPS

Retain "Sump-Pump Basins and Basin Covers" Article if retaining this article.

Submersible, Fixed-Position, Single-Seal Sump Pumps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Barnes; Crane Pumps & Systems.

Bell & Gossett Domestic Pump; ITT Corporation.

Flo Fab inc.

Glentronics, Inc.

Goulds Pumps; ITT Corporation.

Grundfos Pumps Corp.

Liberty Pumps.

Little Giant Pump Co.

McDonald, A. Y. Mfg. Co.

Pentair Pump Group; Hydromatic Pumps.

Pentair Pump Group; Myers.

Stancor, Inc.

Sta-Rite Industries, Inc.

Weil Pump Company, Inc.

Weinman Division; Crane Pumps & Systems.

Zoeller Company.

<Insert manufacturer's name>.

Description:  Factory-assembled and -tested sump-pump unit.

Pump Type:  Submersible, end-suction, single-stage, close-coupled, overhung-impeller, centrifugal sump pump as defined in HI 1.1-1.2 and HI 1.3.

Pump Casing:  Cast iron, with strainer inlet, legs that elevate pump to permit flow into impeller, and vertical discharge for piping connection.

If Project has more than one type or configuration of sump pump, retain appropriate options in first subparagraph below and indicate impeller material for each pump in schedule on Drawings.  See sample schedule in Evaluations.

Impeller:  Statically and dynamically balanced, [ASTM A 48/A 48M, Class No. 25 A cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [and] [ASTM B 584, cast bronze], [semiopen] <Insert design> design for clear wastewater handling, and keyed and secured to shaft.

Pump and Motor Shaft:  Stainless steel[ or steel], with factory-sealed, grease-lubricated ball bearings.

Seal:  Mechanical.

Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.

Verify that pump selected has motor feature in first subparagraph below, if either is required, or delete.

Motor Housing Fluid:  [Air] [Oil].

Retain one of two "Controls" subparagraphs below.

Controls in first subparagraph below are rod-and-float type.

Controls:

Enclosure:  NEMA 250, [Type 1] [Type 4X] <Insert type>.

Switch Type:  Pedestal-mounted float switch with float rods and rod buttons.

Retain first subparagraph below for duplex pump units.  Revise if unit includes three or more pumps.

Automatic Alternator:  Start pumps on successive cycles and start multiple pumps if one cannot handle load.

Float Guides:  Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

High-Water Alarm:  Cover-mounted, compression-probe alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Controls in first subparagraph below are float- and pressure-switch types.

Controls:

Enclosure:  NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall]-mounted.

Switch Type:  [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain first subparagraph below for duplex pump units.  Revise if unit includes three or more pumps.

Automatic Alternator:  Start pumps on successive cycles and start multiple pumps if one cannot handle load.

High-Water Alarm:  Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Control-Interface Features:

Two subparagraphs below are optional control features.

Remote Alarm Contacts:  For remote alarm interface.

Building Automation System Interface:  Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

On-off status of pump.

Alarm status.

Submersible, Fixed-Position, Double-Seal Sump Pumps:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

BJM Pumps, LLC.

EBARA Fluid Handling.

ITT Flygt Corporation.

PACO Pumps; Grundfos Pumps Corporation, U.S.A.

<Insert manufacturer's name>.

Description:  Factory-assembled and -tested sump-pump unit.

Pump Type:  Submersible, end-suction, single-stage, close-coupled, overhung-impeller, centrifugal sump pump as defined in HI 1.1-1.2 and HI 1.3.

Pump Casing:  Cast iron, with strainer inlet, legs that elevate pump to permit flow into impeller, and vertical discharge for piping connection.

If Project has more than one type or configuration of sump pump, retain appropriate options in first subparagraph below and indicate impeller material for each pump in schedule on Drawings.  See sample schedule in Evaluations.

Impeller:  Statically and dynamically balanced, [ASTM A 48/A 48M, Class No. 25 A cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [and] [ASTM B 584, cast bronze], [semiopen] <Insert design> design for clear wastewater handling, and keyed and secured to shaft.

Pump and Motor Shaft:  Stainless steel[ or steel], with factory-sealed, grease-lubricated ball bearings.

Seals:  Mechanical.

Verify that pump selected has feature in first subparagraph below, if required, or delete.

Moisture-Sensing Probe:  Internal moisture sensor and moisture alarm.

Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.

Verify that pump selected has motor feature in first subparagraph below, if either is required, or delete.

Motor Housing Fluid:  [Air] [Oil].

Retain one of two "Controls" subparagraphs below.

Controls in first subparagraph below are rod-and-float type.

Controls:

Enclosure:  NEMA 250, [Type 1] [Type 4X] <Insert type>.

Switch Type:  Pedestal-mounted float switch with float rods and rod buttons.

Retain first subparagraph below for duplex pump units.  Revise if unit includes three or more pumps.

Automatic Alternator:  Start pumps on successive cycles and start multiple pumps if one cannot handle load.

Float Guides:  Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

High-Water Alarm:  Cover-mounted, compression-probe alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Controls in first subparagraph below are float- and pressure-switch types.

Controls:

Enclosure:  NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall]-mounted.

Switch Type:  [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain first subparagraph below for duplex pump units.  Revise if unit includes three or more pumps.

Automatic Alternator:  Start pumps on successive cycles and start multiple pumps if one cannot handle load.

High-Water Alarm:  Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Control-Interface Features:

Two subparagraphs below are optional control features.

Remote Alarm Contacts:  For remote alarm interface.

Building Automation System Interface:  Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

On-off status of pump.

Alarm status.

WET-PIT-VOLUTE SUMP PUMPS

Retain "Sump-Pump Basins and Basin Covers" Article if retaining this article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Alyan Pump Company.

Armstrong Pumps Inc.

Chicago Pump Company; a division of Yeomans Chicago Corporation.

Federal Pump Corp.

Flo Fab inc.

PACO Pumps; Grundfos Pumps Corporation, U.S.A.

Peerless Pump, Inc.

Pentair Pump Group; Aurora Pump.

Swaby Manufacturing Company.

Tramco Pump Company.

Vertiflo Pump Company.

Weil Pump Company, Inc.

Weinman Division; Crane Pumps & Systems.

Yeomans Chicago Corporation.

<Insert manufacturer's name>.

Description:  Factory-assembled and -tested sump-pump unit.

Pump Type:  Wet-pit-volute, single-stage, separately-coupled, overhung-impeller, centrifugal sump pump as defined in HI 1.1-1.2 and HI 1.3.

Pump Casing:  Cast iron, with strainer inlet and threaded connection for NPS 2 (DN 50) and smaller and flanged connection for NPS 2-1/2 (DN 65) and larger discharge piping.

If Project has more than one type or configuration of sump pump, retain appropriate options in first paragraph below and indicate impeller material for each pump in schedule on Drawings.  See sample schedule in Evaluations.

Impeller:  Statically and dynamically balanced, [ASTM A 48/A 48M, Class No. 25 A cast iron] [ASTM A 532/A 532M, abrasion-resistant cast iron] [and] [ASTM B 584, cast bronze], [semiopen] <Insert design> design for clear wastewater handling, and keyed and secured to shaft.

Sleeve Bearings:  Bronze.  Include oil-lubricated, intermediate sleeve bearings at 48-inch (1200-mm) maximum intervals if basin depth is more than 48 inches (1200 mm), and grease-lubricated, ball-type thrust bearings.

Pump and Motor Shaft Coupling:  Flexible, capable of absorbing torsional vibration and shaft misalignment.

Pump Discharge Piping:  Factory or field fabricated, [galvanized, ASTM A 53/A 53M, Schedule 40, steel pipe with ASME B16.1, Class 125, cast-iron flanges and flanged fittings or ASME B16.4, Class 125, gray iron threaded fittings] <Insert pipe material>.

Support Plate:  Cast iron or coated steel and strong enough to support pumps, motors, and controls.  Refer to Part 2 "Sump-Pump Basins and Basin Covers" Article for requirements.

Shaft Seal:  Stuffing box, with graphite-impregnated braided-yarn rings and bronze packing gland.

Motor:  Single-speed; grease-lubricated ball bearings and mounting on vertical, cast-iron pedestal.

Retain one of two "Controls" paragraphs below.

Controls in first paragraph below are rod-and-float type.

Controls:

Enclosure:  NEMA 250, [Type 1] [Type 4X] <Insert type>.

Switch Type:  Pedestal-mounted float switch with float rods and rod buttons.

Retain first subparagraph below for duplex pump units.  Revise if unit includes three or more pumps.

Automatic Alternator:  Start pumps on successive cycles and start multiple pumps if one cannot handle load.

Float Guides:  Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

High-Water Alarm:  Cover-mounted, compression-probe alarm, with electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Controls in first paragraph below are float- and pressure-switch types.

Controls:

Enclosure:  NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall]-mounted.

Switch Type:  [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain first subparagraph below for duplex pump units.  Revise if unit includes three or more pumps.

Automatic Alternator:  Start pumps on successive cycles and start multiple pumps if one cannot handle load.

High-Water Alarm:  Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120-V ac, with transformer and contacts for remote alarm bell.

Control-Interface Features:

Two subparagraphs below are optional control features.

Remote Alarm Contacts:  For remote alarm interface.

Building Automation System Interface:  Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

On-off status of pump.

Alarm status.

SUMP PUMP CAPACITIES AND CHARACTERISTICS

If Project has more than one sump pump, delete this article and schedule sump pumps on Drawings.  See sample schedule in Evaluations.

Unit Capacity:  <Insert gpm (L/minute)>.

Number of Pumps:  [One] [Two] <Insert number>.

Each Pump:

Capacity:  <Insert gpm (L/minute)>.

Total Dynamic Head:  <Insert feet (kPa)>.

Speed:  <Insert rpm>.

Discharge Size:  <Insert NPS (DN)>.

Electrical Characteristics:

Motor Horsepower:  <Insert value>.

Volts:  [120] [240] [277] [480] <Insert value>.

Phases:  [Single] [Three].

Hertz:  60.

Unit Electrical Characteristics:

Full-Load Amperes:  <Insert value>.

Minimum Circuit Ampacity:  <Insert value>.

Maximum Overcurrent Protection:  <Insert value> A.

SUMP-PUMP BASINS AND BASIN COVERS

Retain this article if retaining one or both of "Submersible Sump Pumps" or "Wet-Pit-Volute Sump Pumps" articles.

Sump-pump basins typically are round with space for simplex or multiplex pumps.

Basins:  Factory-fabricated, watertight, cylindrical, basin sump with top flange and sidewall openings for pipe connections.

Material:  [Cast iron] [Fiberglass] [Polyethylene] <Insert material>.

Reinforcement:  Mounting plates for pumps, fittings, and accessories.

Retain subparagraph below if required to anchor basin to concrete slab in case of ground-water problems.

Anchor Flange:  Same material as or compatible with basin sump, cast in or attached to sump, in location and of size required to anchor basin in concrete slab.

Sump-pump basin covers typically are round with openings for simplex or multiplex pumps.

Basin Covers:  Fabricate metal cover with openings having gaskets, seals, and bushings; for access to pumps, pump shafts, control rods, discharge piping, vent connections, and power cables.

Reinforcement:  Steel or cast iron, capable of supporting foot traffic for basins installed in foot-traffic areas.

If Project has more than one type or configuration of sump-pump basin, delete paragraph below and schedule sump-pump basins on Drawings.  See sample schedule in Evaluations.

Capacities and Characteristics:

Capacity:  <Insert gal (L)>.

Diameter:  <Insert inches (mm)>.

Depth:  <Insert inches (mm)>.

Inlet No. 1:

Drainage Pipe Size:  <Insert NPS (DN)>.

Bottom of Sump to Centerline:  <Insert inches (mm)>.

Type:  [Flanged] [Hubbed] [Threaded] outside.

Inlet No. 2:

Drainage Pipe Size:  <Insert NPS (DN)>.

Bottom of Sump to Centerline:  <Insert inches (mm)>.

Type:  [Flanged] [Hubbed] [Threaded] outside.

Inlet No. 3:

Drainage Pipe Size:  <Insert NPS (DN)>.

Bottom of Sump to Centerline:  <Insert inches (mm)>.

Type:  [Flanged] [Hubbed] [Threaded] outside.

Sidewall Outlet:

Discharge Pipe Size:  <Insert NPS (DN)>.

Bottom of Sump to Centerline:  <Insert inches (mm)>.

Type:  [Hubbed inside] [Hubbed outside] <Insert type>.

Cover Material:  [Cast iron] [Steel with bituminous coating] [Cast iron or steel with bituminous coating] <Insert material>.

Cover Diameter:  <Insert inches (mm)>, but not less than outside diameter of basin top flange.

Manhole Required in Cover:  [Yes] [No].

Vent Size:  [Not required] <Insert NPS (DN)>.

PACKAGED DRAINAGE-PUMP UNITS

Packaged Pedestal Drainage-Pump Units:

Units in this paragraph are complete with a pump and controls, and typically are installed in a pit.  Units have limited applications and capacities.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

AMT; a subsidiary of the Gorman-Rupp Company.

Goulds Pumps; ITT Corporation.

Liberty Pumps.

Little Giant Pump Co.

Pentair Pump Group; Hydromatic Pumps.

Pentair Pump Group; Myers.

Sta-Rite Industries, Inc.

Zoeller Company.

<Insert manufacturer's name>.

Description:  Factory-assembled and -tested, automatic-operation, freestanding, sump-pump unit.

Pump Type:  Wet-pit-volute, single-stage, separately-coupled, overhung-impeller centrifugal pump as defined in HI 1.1-1.2 and HI 1.3.

Pump Casing:  Corrosion-resistant material, with strainer inlet, design that permits flow into impeller, and vertical discharge for piping connection.

Impeller:  Aluminum, brass, or plastic.

Motor:  With built-in overload protection and mounted vertically on sump pump column.

Power Cord:  Three-conductor, waterproof cable of length required but not less than 72 inches (1830 mm), with grounding plug and cable-sealing assembly for connection at pump.

Control:  Float switch.

Packaged Submersible Drainage-Pump Units:

Units in this paragraph are complete with a pump, basin and cover, piping, and controls.  Units have limited applications and capacities.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

ABS Pumps Inc.

Bell & Gossett Domestic Pump; ITT Corporation.

Glentronics, Inc.

Goulds Pumps; ITT Corporation.

Grundfos Pumps Corp.

Liberty Pumps.

Little Giant Pump Co.

McDonald, A. Y. Mfg. Co.

Pentair Pump Group; Hydromatic Pumps.

Pentair Pump Group; Myers.

Sta-Rite Industries, Inc.

Zoeller Company.

<Insert manufacturer's name>.

Description:  Factory-assembled and -tested, automatic-operation, basin-mounted, sump-pump unit.

Pump Type:  Submersible, end-suction, single-stage, close-coupled, overhung-impeller centrifugal pump as defined in HI 1.1-1.2 and HI 1.3.

Casing:  [Metal] <Insert material>.

Impeller:  [Brass] <Insert material>.

Pump Seal:  Mechanical.

Motor:  Hermetically sealed, capacitor-start type, with built-in overload protection.

Power Cord:  Three-conductor, waterproof cable of length required but not less than 72 inches (1830 mm), with grounding plug and cable-sealing assembly for connection at pump.

Pump Discharge Piping:  Factory or field fabricated, [galvanized, ASTM A 53/A 53M, Schedule 40, steel pipe with ASME B16.4, Class 125, gray iron threaded fittings] <Insert pipe material>.

Control:  Motor-mounted float switch.

Basin:  Plastic.

If Project has more than one packaged drainage-pump unit, delete paragraph below and schedule packaged drainage-pump units on Drawings.

Capacity and Characteristics:

Capacity:  <Insert gpm (L/minute)>.

Total Dynamic Head:  <Insert feet (kPa)>.

Speed:  <Insert rpm>.

Discharge Pipe Size:  <Insert NPS (DN)>.

Electrical Characteristics:

Motor Horsepower:  <Insert value>.

Volts:  [120] [240] [277] [480] <Insert value>.

Phases:  [Single] [Three].

Hertz:  60.

Full-Load Amperes:  <Insert value>.

Minimum Circuit Ampacity:  <Insert value>.

Maximum Overcurrent Protection:  <Insert value> A.

Retain first subparagraph below for packaged pedestal drainage-pump units.

Basin:  Not Required.

Retain subparagraph below for packaged submersible drainage-pump units.

Basin:

Capacity:  [2 gal (7.6 L)] [5 gal (18.9 L)] <Insert other> minimum.

Inlet Connection:  [NPS 1-1/2 (DN 40)] <Insert other> minimum.

MOTORS

Default motor characteristics are specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

Motors for submersible pumps shall be hermetically sealed.

EXECUTION

EARTHWORK

Excavation and filling are specified in Section 312000 "Earth Moving."

EXAMINATION

Examine roughing-in for plumbing piping to verify actual locations of storm drainage piping connections before sump pump installation.

INSTALLATION

Pump Installation Standards:  Comply with HI 1.4 for installation of sump pumps.

CONNECTIONS

Coordinate pump installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Comply with requirements for piping specified in Section 221413 "Facility Storm Drainage Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

Install piping adjacent to equipment to allow service and maintenance.

FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

Tests and Inspections:

Perform each visual and mechanical inspection.

Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

Pumps and controls will be considered defective if they do not pass tests and inspections.

Prepare test and inspection reports.

STARTUP SERVICE

[Engage a factory-authorized service representative to perform] [Perform] startup service.

Complete installation and startup checks according to manufacturer's written instructions.

<Insert startup steps if any>.

ADJUSTING

Adjust pumps to function smoothly, and lubricate as recommended by manufacturer.

Adjust control set points.

DEMONSTRATION

[Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain[ controls and] pumps.

END OF SECTION 221429