SECTION 211200 - FIRE-SUPPRESSION STANDPIPES

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Pipes, fittings, and specialties.

Fire-protection valves.

Hose connections.

Hose stations.

Monitors.

Fire-department connections.

Alarm devices.

Manual control stations.

Control panels.

Pressure gages.

Related Sections:

Section 211313 "Wet-Pipe Sprinkler Systems" for wet-pipe sprinkler piping.

Section 211316 "Dry-Pipe Sprinkler Systems" for dry-pipe sprinkler piping.

Section 211339 "Foam-Water Systems" for AFFF piping.

[Section 213113 "Electric-Drive, Centrifugal Fire Pumps"] [Section 213116 "Diesel-Drive, Centrifugal Fire Pumps"] [Section 213213 "Electric-Drive, Vertical-Turbine Fire Pumps"] [Section 213216 "Diesel-Drive, Vertical-Turbine Fire Pumps"] for fire pumps, pressure-maintenance pumps, and fire-pump controllers.

[Section 283111 "Digital, Addressable Fire-Alarm System"] [Section 283112 "Zoned (DC Loop) Fire-Alarm System"] for alarm devices not specified in this Section.

DEFINITIONS

High-Pressure Standpipe Piping:  Fire-suppression standpipe piping designed to operate at working pressure higher than standard 175 psig (1200 kPa), but not higher than [250 psig (1725 kPa)] [300 psig (2070 kPa)].

Standard-Pressure Standpipe Piping:  Fire-suppression standpipe piping designed to operate at working pressure 175 psig (1200 kPa) maximum.

SYSTEM DESCRIPTIONS

Automatic Wet-Type, Class I Standpipe System:  Includes NPS 2-1/2 (DN 65) hose connections.  Has open water-supply valve with pressure maintained and is capable of supplying water demand.

Automatic Wet-Type, Class II Standpipe System:  Includes NPS 1-1/2 (DN 40) hose stations.  Has open water-supply valve with pressure maintained and is capable of supplying water demand.

Automatic Wet-Type, Class III Standpipe System:  Includes NPS 1-1/2 (DN 40) hose stations and NPS 2-1/2 (DN 65) hose connections.  Has open water-supply valve with pressure maintained and is capable of supplying water demand.

Automatic Dry-Type, Class I Standpipe System:  Includes NPS 2-1/2 (DN 65) hose connections.  Has open water-supply valve and dry-pipe valve with standpipes containing compressed air.  Opening fire-hose valve releases compressed air and permits water pressure to open dry-pipe valve.  Water then flows into standpipes.

Automatic Dry-Type, Class II Standpipe System:  Includes NPS 1-1/2 (DN 40) hose stations.  Has open water-supply valve and dry-pipe valve with standpipes containing compressed air.  Opening fire-hose valve releases compressed air and permits water pressure to open dry-pipe valve.  Water then flows into standpipes.

Automatic Dry-Type, Class III Standpipe System:  Includes NPS 1-1/2 (DN 40) hose stations and NPS 2-1/2 (DN 65) hose connections.  Has open water-supply valve and dry-pipe valve with standpipes containing compressed air.  Opening fire-hose valve releases compressed air and permits water pressure to open dry-pipe valve.  Water then flows into standpipes.

Semiautomatic Dry-Type, Class I Standpipe System:  Includes NPS 2-1/2 (DN 65) hose connections.  Has open water-supply valve and deluge valve with standpipes containing air.  Actuation of detection device permits water pressure to open deluge valve.  Water then flows into standpipes.

Semiautomatic Dry-Type, Class II Standpipe System:  Includes NPS 1-1/2 (DN 40) hose stations.  Has open water-supply valve and deluge valve with standpipes containing air.  Actuation of detection device permits water pressure to open deluge valve.  Water then flows into standpipes.

Semiautomatic Dry-Type, Class III Standpipe System:  Includes NPS 1-1/2 (DN 40) hose stations and NPS 2-1/2 (DN 65) hose connections.  Has open water-supply valve and deluge valve with standpipes containing air.  Actuation of detection device permits water pressure to open deluge valve.  Water then flows into standpipes.

Manual Wet-Type, Class I Standpipe System:  Includes NPS 2-1/2 (DN 65) hose connections.  Has small water supply to maintain water in standpipes.  Piping is wet, but water must be pumped into standpipes to satisfy demand.

Manual Dry-Type, Class I Standpipe System:  Includes NPS 2-1/2 (DN 65) hose connections.  Does not have permanent water supply.  Piping is dry.  Water must be pumped into standpipes to satisfy demand.

PERFORMANCE REQUIREMENTS

Standard-Pressure, Fire-Suppression Standpipe System Component:  Listed for 175-psig (1200-kPa) minimum working pressure.

High-Pressure, Fire-Suppression Standpipe System Component:  Listed for [250-psig (1725-kPa) minimum] [300-psig (2070-kPa)] working pressure.

Delegated Design:  Design fire-suppression standpipes, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Available fire-hydrant flow test records indicate the following conditions:

Fire-suppression standpipe design shall be approved by authorities having jurisdiction.

Minimum residual pressure at each hose-connection outlet is as follows:

Maximum residual pressure at required flow at each hose-connection outlet is as follows unless otherwise indicated:

ACTION SUBMITTALS

Product Data:  For each type of product indicated.[  Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.]

Shop Drawings:  For fire-suppression standpipes.  Include plans, elevations, sections, details, and attachments to other work.

Wiring Diagrams:  For power, signal, and control wiring.

Delegated-Design Submittal:  For standpipe systems indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

INFORMATIONAL SUBMITTALS

Coordination Drawings:  Fire-suppression standpipes, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

Domestic water piping.

Compressed air piping.

HVAC hydronic piping.

Qualification Data:  For qualified Installer[ and professional engineer].

Approved Standpipe Drawings:  Working plans, prepared according to NFPA 14, that have been approved by authorities having jurisdiction, including hydraulic calculations if applicable.

Welding certificates.

Fire-hydrant flow test report.

Field Test Reports and Certificates:  Indicate and interpret test results for compliance with performance requirements and as described in NFPA 14.  Include "Contractor's Material and Test Certificate for Aboveground Piping" and "Contractor's Material and Test Certificate for Underground Piping."

Field quality-control reports.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:  For fire-suppression standpipes specialties to include in emergency, operation, and maintenance manuals.

QUALITY ASSURANCE

Installer Qualifications:

Installer's responsibilities include designing, fabricating, and installing fire-suppression standpipes and providing professional engineering services needed to assume engineering responsibility.  Base calculations on results of fire-hydrant flow test.

Engineering Responsibility:  Preparation of working plans, calculations, and field test reports by a qualified professional engineer.

Welding Qualifications:  Qualify procedures and operators according to ASME Boiler and Pressure Vessel Code.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

NFPA Standards:  Fire-suppression standpipe equipment, specialties, accessories, installation, and testing shall comply with NFPA 14, "Installation of Standpipe and Hose Systems."

PROJECT CONDITIONS

Interruption of Existing Fire-Suppression Standpipe Service:  Do not interrupt fire-suppression standpipe service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary fire-suppression standpipe service according to requirements indicated:

Do not proceed with interruption of fire-suppression standpipe service without [Architect's] [Construction Manager's] [Owner's] written permission.

PRODUCTS

PIPING MATERIALS

Comply with requirements in "Piping Schedule" Article for applications of pipe, tube, and fitting materials, and for joining methods for specific services, service locations, and pipe sizes.

STEEL PIPE AND FITTINGS

Thinwall [Galvanized-] [and] [Black-]Steel Pipe:  ASTM A 135 or ASTM A 795/A 795M, threadable, with wall thickness less than Schedule 30 and equal to or greater than Schedule 10.  Pipe ends may be factory or field formed to match joining method.

Schedule 10, Black-Steel Pipe:  ASTM A 135 or ASTM A 795/A 795M, Schedule 10 in NPS 5 (DN 125) and smaller; and NFPA 13-specified wall thickness in NPS 6 to NPS 10 (DN 150 to DN 250), plain end.

Nonstandard OD, Thinwall Black-Steel Pipe:  ASTM A 135 or ASTM A 795/A 795M, thinwall, with plain ends and wall thickness less than Schedule 10.

Hybrid Black-Steel Pipe:  ASTM A 135 or ASTM A 795/A 795M, lightwall, with wall thickness less than Schedule 10 and greater than Schedule 5.

Standard-Weight, [Galvanized-] [and] [Black-]Steel Pipe Nipples:  ASTM A 733, made of ASTM A 53/A 53M, seamless steel pipe with threaded ends.

[Galvanized] [and] [Uncoated], Steel Couplings:  ASTM A 865, threaded.

[Galvanized] [and] [Uncoated], Gray-Iron Threaded Fittings:  ASME B16.4, Class 125, standard pattern.

Malleable- or Ductile-Iron Unions:  UL 860.

Cast-Iron Flanges:  ASME B16.1, Class 125.

Steel Flanges and Flanged Fittings:  ASME B16.5, Class 150.

Steel Welding Fittings:  ASTM A 234/A 234M and ASME B16.9.

Grooved-Joint, Steel-Pipe Appurtenances:

Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Anvil International, Inc.

Corcoran Piping System Co.

National Fittings, Inc.

Shurjoint Piping Products.

Tyco Fire & Building Products LP.

Victaulic Company.

Pressure Rating:  [175 psig (1200 kPa)] [250 psig (1725 kPa)] [300 psig (2070 kPa)] minimum.

[Galvanized] [and] [Uncoated], Grooved-End Fittings for Steel Piping:  ASTM A 47/A 47M, malleable-iron casting or ASTM A 536, ductile-iron casting; with dimensions matching steel pipe.

Grooved-End-Pipe Couplings for Steel Piping:  AWWA C606 and UL 213, rigid pattern, unless otherwise indicated, for steel-pipe dimensions.  Include ferrous housing sections, EPDM-rubber gasket, and bolts and nuts.

COPPER TUBE AND FITTINGS

Hard Copper Tube:  [ASTM B 88, Type L (ASTM B 88M, Type B)] [and] [ASTM B 88, Type M (ASTM B 88M, Type C)] water tube, drawn temper.

Cast-Copper, Solder-Joint Fittings:  ASME B16.18, pressure fittings.

Wrought-Copper, Solder-Joint Fittings:  ASME B16.22, pressure fittings.

Bronze Flanges:  ASME B16.24, Class 150, with solder-joint ends.

Copper Unions:  MSS SP-123, cast-copper-alloy, hexagonal-stock body, with ball-and-socket, metal-to-metal seating surfaces, and solder-joint or threaded ends.

Grooved-Joint, Copper-Tube Appurtenances:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Anvil International, Inc.

Shurjoint Piping Products.

Victaulic Company.

Grooved-End, Copper Fittings:  ASTM B 75 (ASTM B 75M), copper tube or ASTM B 584, bronze castings.

Grooved-End-Tube Couplings:  To fit copper tube dimensions, with design similar to AWWA C606.  Include ferrous housing sections, EPDM-rubber gasket suitable for hot and cold water, and bolts and nuts.

PIPING JOINING MATERIALS

Pipe-Flange Gasket Materials:  [AWWA C110, rubber, flat face, 1/8 inch (3.2 mm) thick] [or] [ASME B16.21, nonmetallic and asbestos free].

Class 125, Cast-Iron Flanges and Class 150, Bronze Flat-Face Flanges:  Full-face gaskets.

Class 250, Cast-Iron Flanges and Class 300, Steel Raised-Face Flanges:  Ring-type gaskets.

Metal, Pipe-Flange Bolts and Nuts:  ASME B18.2.1, carbon steel unless otherwise indicated.

Brazing Filler Metals:  AWS A5.8/A5.8M, BCuP Series, copper-phosphorus alloys for general-duty brazing unless otherwise indicated.

Welding Filler Metals:  Comply with AWS D10.12M/D10.12 for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

LISTED FIRE-PROTECTION VALVES

General Requirements:

Valves shall be UL listed or FM approved.

Minimum Pressure Rating for Standard-Pressure Piping:  175 psig (1200 kPa).

Minimum Pressure Rating for High-Pressure Piping:  [250 psig (1725 kPa)] [300 psig (2070 kPa)].

Ball Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Anvil International, Inc.

Victaulic Company.

Standard:  UL 1091 except with ball instead of disc.

Valves NPS 1-1/2 (DN 40) and Smaller:  Bronze body with threaded ends.

Valves NPS 2 and NPS 2-1/2 (DN 50 and DN 65):  Bronze body with threaded ends or ductile-iron body with grooved ends.

Valves NPS 3 (DN 80):  Ductile-iron body with grooved ends.

Bronze Butterfly Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Fivalco Inc.

Global Safety Products, Inc.

Milwaukee Valve Company.

Standard:  UL 1091.

Pressure Rating:  175 psig (1200 kPa).

Body Material:  Bronze.

End Connections:  Threaded.

Iron Butterfly Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Anvil International, Inc.

Fivalco Inc.

Global Safety Products, Inc.

Kennedy Valve; a division of McWane, Inc.

Milwaukee Valve Company.

NIBCO INC.

Pratt, Henry Company.

Shurjoint Piping Products.

Tyco Fire & Building Products LP.

Victaulic Company.

Standard:  UL 1091.

Pressure Rating:  175 psig (1200 kPa).

Body Material:  Cast or ductile iron.

Style:  Lug or wafer.

End Connections:  Grooved.

Check Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

American Cast Iron Pipe Company; Waterous Company Subsidiary.

Anvil International, Inc.

Clow Valve Company; a division of McWane, Inc.

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Fire-End & Croker Corporation.

Fire Protection Products, Inc.

Fivalco Inc.

Globe Fire Sprinkler Corporation.

Groeniger & Company.

Kennedy Valve; a division of McWane, Inc.

Matco-Norca.

Metraflex, Inc.

Milwaukee Valve Company.

Mueller Co.; Water Products Division.

NIBCO INC.

Potter Roemer.

Reliable Automatic Sprinkler Co., Inc.

Shurjoint Piping Products.

Tyco Fire & Building Products LP.

United Brass Works, Inc.

Venus Fire Protection Ltd.

Victaulic Company.

Viking Corporation.

Watts Water Technologies, Inc.

Standard:  UL 312.

Pressure Rating:  [250 psig (1725 kPa) minimum] [300 psig (2070 kPa)].

Type:  Swing check.

Body Material:  Cast iron.

End Connections:  Flanged or grooved.

Bronze OS&Y Gate Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Milwaukee Valve Company.

NIBCO INC.

United Brass Works, Inc.

Standard:  UL 262.

Pressure Rating:  175 psig (1200 kPa).

Body Material:  Bronze.

End Connections:  Threaded.

Iron OS&Y Gate Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

American Cast Iron Pipe Company; Waterous Company Subsidiary.

American Valve, Inc.

Clow Valve Company; a division of McWane, Inc.

Crane Co.; Crane Valve Group; Crane Valves.

Crane Co.; Crane Valve Group; Jenkins Valves.

Crane Co.; Crane Valve Group; Stockham Division.

Hammond Valve.

Milwaukee Valve Company.

Mueller Co.; Water Products Division.

NIBCO INC.

Shurjoint Piping Products.

Tyco Fire & Building Products LP.

United Brass Works, Inc.

Watts Water Technologies, Inc.

Standard:  UL 262.

Pressure Rating:  [250 psig (1725 kPa) minimum] [300 psig (2070 kPa)].

Body Material:  Cast or ductile iron.

End Connections:  Flanged or grooved.

Indicating-Type Butterfly Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Anvil International, Inc.

Fivalco Inc.

Global Safety Products, Inc.

Kennedy Valve; a division of McWane, Inc.

Milwaukee Valve Company.

NIBCO INC.

Shurjoint Piping Products.

Tyco Fire & Building Products LP.

Victaulic Company.

Standard:  UL 1091.

Pressure Rating:  175 psig (1200 kPa) minimum.

Valves NPS 2 (DN 50) and Smaller:

Valve Type:  Ball or butterfly.

Body Material:  Bronze.

End Connections:  Threaded.

Valves NPS 2-1/2 (DN 65) and Larger:

Valve Type:  Butterfly.

Body Material:  Cast or ductile iron.

End Connections:  Flanged, grooved, or wafer.

Valve Operation:  Integral [electrical, 115-V ac, prewired, single-circuit, supervisory switch] [electrical, 115-V ac, prewired, two-circuit, supervisory switch] [visual] indicating device.

NRS Gate Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

American Cast Iron Pipe Company; Waterous Company Subsidiary.

American Valve, Inc.

Clow Valve Company; a division of McWane, Inc.

Crane Co.; Crane Valve Group; Stockham Division.

Kennedy Valve; a division of McWane, Inc.

Mueller Co.; Water Products Division.

NIBCO INC.

Tyco Fire & Building Products LP.

Standard:  UL 262.

Pressure Rating:  [250 psig (1725 kPa) minimum] [300 psig (2070 kPa)].

Body Material:  Cast iron with indicator post flange.

Stem:  Nonrising.

End Connections:  Flanged or grooved.

Indicator Posts:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

American Cast Iron Pipe Company; Waterous Company Subsidiary.

American Valve, Inc.

Clow Valve Company; a division of McWane, Inc.

Crane Co.; Crane Valve Group; Stockham Division.

Kennedy Valve; a division of McWane, Inc.

Mueller Co.; Water Products Division.

NIBCO INC.

Tyco Fire & Building Products LP.

Standard:  UL 789.

Type:  Horizontal for wall mounting.

Body Material:  Cast iron with extension rod and locking device.

Operation:  [Wrench] [Hand wheel].

TRIM AND DRAIN VALVES

General Requirements:

Standard:  UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

Pressure Rating:  175 psig (1200 kPa) minimum.

Angle Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Fire Protection Products, Inc.

United Brass Works, Inc.

Ball Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Affiliated Distributors.

Anvil International, Inc.

Barnett.

Conbraco Industries, Inc.; Apollo Valves.

Fire-End & Croker Corporation.

Fire Protection Products, Inc.

Flowserve.

FNW.

Jomar International, Ltd.

Kennedy Valve; a division of McWane, Inc.

Kitz Corporation.

Legend Valve.

Metso Automation USA Inc.

Milwaukee Valve Company.

NIBCO INC.

Potter Roemer.

Red-White Valve Corporation.

Southern Manufacturing Group.

Stewart, M. A. and Sons Ltd.

Tyco Fire & Building Products LP.

Victaulic Company.

Watts Water Technologies, Inc.

Globe Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Fire Protection Products, Inc.

United Brass Works, Inc.

Plug Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Southern Manufacturing Group.

SPECIALTY VALVES

General Requirements:

Standard:  UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.

Pressure Rating:

Standard-Pressure Piping Specialty Valves:  175 psig (1200 kPa) minimum.

High-Pressure Piping Specialty Valves:  [250 psig (1725 kPa) minimum] [300 psig (2070 kPa)].

Body Material:  Cast or ductile iron.

Size:  Same as connected piping.

End Connections:  Flanged or grooved.

Alarm Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Globe Fire Sprinkler Corporation.

Reliable Automatic Sprinkler Co., Inc.

Tyco Fire & Building Products LP.

Venus Fire Protection Ltd.

Victaulic Company.

Viking Corporation.

Standard:  UL 193.

Design:  For horizontal or vertical installation.

Include trim sets for bypass, drain, electrical sprinkler alarm switch, pressure gages,[ retarding chamber,] and fill-line attachment with strainer.

Drip Cup Assembly:  Pipe drain without valves and separate from main drain piping.

Drip Cup Assembly:  Pipe drain with check valve to main drain piping.

Dry-Pipe Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Globe Fire Sprinkler Corporation.

Reliable Automatic Sprinkler Co., Inc.

Tyco Fire & Building Products LP.

Venus Fire Protection Ltd.

Victaulic Company.

Viking Corporation.

Standard:  UL 260.

Design:  Differential-pressure type.

Include UL 1486, quick-opening devices, trim sets for air supply, drain, priming level, alarm connections, ball drip valves, pressure gages, priming chamber attachment, and fill-line attachment.

Air-Pressure Maintenance Device:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Globe Fire Sprinkler Corporation.

Reliable Automatic Sprinkler Co., Inc.

Tyco Fire & Building Products LP.

Venus Fire Protection Ltd.

Victaulic Company.

Viking Corporation.

Standard:  UL 260.

Type:  Automatic device to maintain minimum air pressure in piping.

Include shutoff valves to permit servicing without shutting down sprinkler piping, bypass valve for quick filling, pressure regulator or switch to maintain pressure, strainer, pressure ratings with 14- to 60-psig (95- to 410-kPa) adjustable range, and [175-psig (1200-kPa)] [300-psig (2070-kPa)] outlet pressure.

Air Compressor:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Gast Manufacturing Inc.

General Air Products, Inc.

Viking Corporation.

Standard:  UL's "Fire Protection Equipment Directory" listing.

Motor Horsepower:  Fractional.

Power:  120-V ac, 60 Hz, single phase.

Deluge Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

BERMAD Control Valves.

CLA-VAL Automatic Control Valves.

Globe Fire Sprinkler Corporation.

OCV Control Valves.

Reliable Automatic Sprinkler Co., Inc.

Tyco Fire & Building Products LP.

Venus Fire Protection Ltd.

Victaulic Company.

Viking Corporation.

Standard:  UL 260.

Design:  Hydraulically operated, differential-pressure type.

Include trim sets for bypass, drain, electrical sprinkler alarm switch, pressure gages, drip cup assembly piped without valves and separate from main drain line, fill-line attachment with strainer, and push-rod chamber supply connection.

Wet, Pilot-Line Trim Set:  Include gage to read push-rod chamber pressure, globe valve for manual operation of deluge valve, and connection for actuation device.

Dry, Pilot-Line Trim Set:  Include dry, pilot-line actuator; air- and water-pressure gages; low-air-pressure warning switch; air relief valve; and actuation device.  Dry, pilot-line actuator includes cast-iron, operated, diaphragm-type valve with resilient facing plate, resilient diaphragm, and replaceable bronze seat.  Valve includes threaded water and air inlets and water outlet.  Loss of air pressure on dry, pilot-line side allows pilot-line actuator to open and causes deluge valve to open immediately.

Air-Pressure Maintenance Device:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Globe Fire Sprinkler Corporation.

Reliable Automatic Sprinkler Co., Inc.

Tyco Fire & Building Products LP.

Venus Fire Protection Ltd.

Victaulic Company.

Viking Corporation.

Standard:  UL 260.

Type:  Automatic device to maintain minimum air pressure in piping.

Include shutoff valves to permit servicing without shutting down sprinkler piping, bypass valve for quick filling, pressure regulator, or switch to maintain pressure, strainer, pressure ratings with 14- to 60-psig (95- to 410-kPa) adjustable range, and [175-psig (1200-kPa)] [300-psig (2070-kPa)] outlet pressure.

Air Compressor:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Gast Manufacturing Inc.

General Air Products, Inc.

Viking Corporation.

Standard:  UL's "Fire Protection Equipment Directory" listing.

Motor Horsepower:  Fractional.

Power:  120-V ac, 60 Hz, single phase.

Pressure-Reducing Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

Fire Protection Products, Inc.

GMR International Equipment Corporation.

Guardian Fire Equipment, Inc.

Potter Roemer.

Tyco Fire & Building Products LP.

Wilson & Cousins Inc.

Zurn Plumbing Products Group; Wilkins Water Control Products Division.

UL 668 hose valve, with integral UL 1468 reducing device.

Pressure Rating:  300 psig (2070 kPa) minimum.

Material:  Brass or bronze.

Inlet:  Female pipe threads.

Outlet:  Threaded with or without adapter having male hose threads.

Pattern:  [Angle] [or] [gate].

Finish:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

Automatic (Ball Drip) Drain Valves:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Reliable Automatic Sprinkler Co., Inc.

Tyco Fire & Building Products LP.

Standard:  UL 1726.

Pressure Rating:  175 psig (1200 kPa) minimum.

Type:  Automatic draining, ball check.

Size:  NPS 3/4 (DN 20).

End Connections:  Threaded.

HOSE CONNECTIONS

Adjustable-Valve Hose Connections:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

Fire Protection Products, Inc.

GMR International Equipment Corporation.

Guardian Fire Equipment, Inc.

Potter Roemer.

Tyco Fire & Building Products LP.

Wilson & Cousins Inc.

Zurn Plumbing Products Group; Wilkins Water Control Products Division.

Standard:  UL 668 hose valve, with integral UL 1468 reducing or restricting pressure-control device, for connecting fire hose.

Pressure Rating:  300 psig (2070 kPa) minimum.

Material:  Brass or bronze.

Size:  NPS 1-1/2 or NPS 2-1/2 (DN 40 or DN 65, as indicated) , as indicated.

Inlet:  Female pipe threads.

Outlet:  Male hose threads with lugged cap, gasket, and chain.  Include hose valve threads according to NFPA 1963 and matching local fire-department threads.

Pattern:  [Angle] [or] [gate].

Pressure-Control Device Type:  Pressure [reducing] [restricting].

Finish:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

Nonadjustable-Valve Hose Connections:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

Fire Protection Products, Inc.

GMR International Equipment Corporation.

Guardian Fire Equipment, Inc.

Kennedy Valve; a division of McWane, Inc.

Mueller Co.; Water Products Division.

NIBCO INC.

Potter Roemer.

Tyco Fire & Building Products LP.

Wilson & Cousins Inc.

Standard:  UL 668 hose valve for connecting fire hose.

Pressure Rating:  300 psig (2070 kPa) minimum.

Material:  Brass or bronze.

Size:  NPS 1-1/2 or NPS 2-1/2 (DN 40 or DN 65), as indicated.

Inlet:  Female pipe threads.

Outlet:  Male hose threads with lugged cap, gasket, and chain.  Include hose valve threads according to NFPA 1963 and matching local fire-department threads.

Pattern:  [Angle] [or] [gate].

Finish:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

NPS 1-1/2 (DN 40) RACK-TYPE HOSE STATIONS

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

American Fire Hose & Cabinet.

Angus; Part of Kidde Fire Fighting Organization.

Brooks Equipment Co., Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

GMR International Equipment Corporation.

Potter Roemer.

Wilson & Cousins Inc.

Hose Rack:

Standard:  UL 47.

Material:  [Brass or bronze with polished chrome-plated] [Steel with red-enamel] finish.

Type:  Hose-rack assembly.  Include hose valve, hose rack, water-retention device, hose pins, and hose.

Operation:  Semiautomatic.

Sized to hold fire hose.

Hose Valve:

Standard:  UL 668 NPS 1-1/2 (DN 40), for connecting fire hose.

Type:  [Adjustable] [Nonadjustable].

Pressure-Control Device:  [Not required] [Pressure reducing] [Pressure reducing or pressure restricting] [Pressure restricting].

Hose Valve and Trim Finish:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

Pressure Rating:  300 psig (2070 kPa) minimum.

Pattern:  Angle.

Material:  Brass or bronze.

Pressure-Control Device:  UL 1468 integral or for field installation if indicated.

Size:  NPS 1-1/2 (DN 40).

Inlet:  Female pipe threads.

Outlet:  Male hose threads according to NFPA 1963 and matching local fire-department threads.

Hose:

Standards:  NFPA 1961 and UL 219 lined fire hose with swivel inlet, coupling, gaskets, and nozzle.

Size:  NPS 1-1/2 (DN 40).

Jacket:  [Combination of natural and synthetic threads] [Natural thread] [Synthetic thread].

Lining:  [Rubber, plastic, or combination of rubber and plastic compounds] [Combination of rubber and plastic compounds] [Rubber compound] [Plastic compound].

Cover:  Rubber, plastic, or combination of rubber and plastic compounds.

Nozzle:  UL 401.

Material:  [Brass] [Polished brass] [Rough chrome-plated brass] [Polished chrome-plated brass] [Polycarbonate plastic].

Type:  [Plain, for nonadjustable water stream] [Spray, adjustable from shutoff to fog spray or straight stream] [Spray, adjustable from shutoff to full fog; for use on electrical fires].

NPS 1-1/2 BY NPS 2-1/2 (DN 40 BY DN 65) RACK-TYPE HOSE STATIONS

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

American Fire Hose & Cabinet.

Angus; Part of Kidde Fire Fighting Organization.

Brooks Equipment Co., Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

GMR International Equipment Corporation.

Potter Roemer.

Wilson & Cousins Inc.

Hose Rack:

Standard:  UL 47.

Material:  [Brass or bronze with polished chrome-plated] [Steel with red-enamel] finish.

Type:  Hose-rack assembly.  Include hose valve, reducer adapter, hose rack, water-retention device, hose pins, and hose.

Operation:  Semiautomatic.

Sized to hold fire hose.

Hose Valve:

Standard:  UL 668, NPS 2-1/2 (DN 65), for connecting fire hose.

Type:  [Adjustable] [Nonadjustable].

Pressure-Control Device:  [Not required] [Pressure reducing] [Pressure reducing or pressure restricting] [Pressure restricting].

Hose Valve and Trim Finish:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

Pressure Rating:  300 psig (2070 kPa) minimum.

Pattern:  Angle.

Material:  Brass or bronze.

Pressure-Control Device:  UL 1468, integral or for field installation if indicated.

Size:  NPS 2-1/2 (DN 65).

Inlet:  Female pipe threads.

Outlet:  Male hose threads according to NFPA 1963 and matching local fire-department threads.

Reducer Adapter:  NPS 2-1/2 by NPS 1-1/2 (DN 65 by DN 40).

Hose:

Standards:  NFPA 1961 and UL 219, lined fire hose with swivel inlet, coupling, gaskets, and nozzle.

Size:  NPS 1-1/2 (DN 40).

Jacket:  [Combination of natural and synthetic threads] [Natural thread] [Synthetic thread].

Lining:  [Rubber, plastic, or combination of rubber and plastic compounds] [Combination of rubber and plastic compounds] [Rubber compound] [Plastic compound].

Cover:  Rubber, plastic, or combination of rubber and plastic compounds.

Nozzle:  UL 401 spray nozzle unless plain nozzle is indicated.

Material:  [Brass] [Polished brass] [Rough chrome-plated brass] [Polished chrome-plated brass] [Polycarbonate plastic].

Type:  [Plain, for nonadjustable water stream] [Spray, adjustable from shutoff to fog spray or straight stream] [Spray, adjustable from shutoff to full fog; for use on electrical fires].

NPS 1-1/2 (DN 40) REEL-TYPE HOSE STATIONS

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Elkhart Brass Mfg. Company, Inc.

Potter Roemer.

Hose Reel:

Standard:  UL 47.

Hose Reel and Bracket Material:  Steel.

Type:  Hose-reel assembly.  Include hose valve, wall bracket, hose reel, water-retention device, hose pins, and hose.

Operation:  Semiautomatic.

Sized to hold fire hose.

Finish:  Red enamel.

Hose Valve:

Standard:  UL 668, NPS 1-1/2 (DN 40), for connecting fire hose.

Type:  [Adjustable] [Nonadjustable].

Pressure-Control Device:  [Not required] [Pressure reducing] [Pressure reducing or pressure restricting] [Pressure restricting].

Hose Valve and Trim Finish:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

Pressure Rating:  300 psig (2070 kPa) minimum.

Pattern:  Angle.

Material:  Brass or bronze.

Pressure-Control Device:  UL 1468, integral or for field installation if indicated.

Size:  NPS 1-1/2 (DN 40).

Inlet:  Female pipe threads.

Outlet:  Male hose threads according to NFPA 1963 and matching local fire-department threads.

Hose:

Standards:  NFPA 1961 and UL 219 lined fire hose with swivel inlet, coupling, gaskets, and nozzle.

Size:  NPS 1-1/2 (DN 40).

Jacket:  [Combination of natural and synthetic threads] [Natural thread] [Synthetic thread].

Lining:  [Rubber, plastic, or combination of rubber and plastic compounds] [Combination of rubber and plastic compounds] [Rubber compound] [Plastic compound].

Cover:  Rubber, plastic, or combination of rubber and plastic compounds.

Nozzle:  UL 401.

Material:  [Brass] [Polished brass] [Rough chrome-plated brass] [Polished chrome-plated brass] [Polycarbonate plastic].

Type:  Spray, adjustable from shutoff to [fog spray or straight stream] [full fog; for use on electrical fires].

MONITORS

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

Guardian Fire Equipment, Inc.

Potter Roemer.

Type:  Stationary.

Nozzle:  UL 401, NPS 2-1/2 (DN 65), brass, adjustable from fog spray to straight stream to shutoff.

Horizontal Rotation:  360 degrees with locking device.

Vertical Rotation:  80-degree elevation and 60-degree depression with locking device.

Waterway:  [Double] [Single] brass or stainless-steel tube.

Operation:  [Lever] [Wheel].

Base Inlet Size:  [NPS 2-1/2 (DN 65)] [NPS 3 (DN 80)] [NPS 4 (DN 100)].

Finish:  Red-painted body with brass trim.

FIRE-DEPARTMENT CONNECTIONS

Exposed-Type, Fire-Department Connection:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

Fire Protection Products, Inc.

GMR International Equipment Corporation.

Guardian Fire Equipment, Inc.

Tyco Fire & Building Products LP.

Wilson & Cousins Inc.

Standard:  UL 405.

Type:  Exposed, projecting, for wall mounting.

Pressure Rating:  175 psig (1200 kPa) minimum.

Body Material:  Corrosion-resistant metal.

Inlets:  Brass with threads according to NFPA 1963 and matching local fire-department sizes and threads.  Include extension pipe nipples, brass lugged swivel connections, and check devices or clappers.

Caps:  Brass, lugged type, with gasket and chain.

Escutcheon Plate:  Round, brass, wall type.

Outlet:  Back, with pipe threads.

Number of Inlets:  [Two] [Three].

Escutcheon Plate Marking:  Similar to "[AUTO SPKR & STANDPIPE] [STANDPIPE]."

Finish:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

Outlet Size:  [NPS 4 (DN 100)] [NPS 5 (DN 125)] [NPS 6 (DN 150)].

Flush-Type, Fire-Department Connection:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Elkhart Brass Mfg. Company, Inc.

GMR International Equipment Corporation.

Guardian Fire Equipment, Inc.

Potter Roemer.

Standard:  UL 405.

Type:  Flush, for wall mounting.

Pressure Rating:  175 psig (1200 kPa) minimum.

Body Material:  Corrosion-resistant metal.

Inlets:  Brass with threads according to NFPA 1963 and matching local fire-department sizes and threads.  Include extension pipe nipples, brass lugged swivel connections, and check devices or clappers.

Caps:  Brass, lugged type, with gasket and chain.

Escutcheon Plate:  Rectangular, brass, wall type.

Outlet:  With pipe threads.

Body Style:  [Horizontal] [Square] [Vertical].

Number of Inlets:  [Two] [Three] [Four] [Six].

Outlet Location:  [Back] [Bottom] [Left side] [Right side] [Top].

Escutcheon Plate Marking:  Similar to "[AUTO SPKR & STANDPIPE] [STANDPIPE]."

Finish:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

Outlet Size:  [NPS 4 (DN 100)] [NPS 5 (DN 125)] [NPS 6 (DN 150)] [NPS 8 (DN 200)].

Yard-Type, Fire-Department Connection:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

Fire Protection Products, Inc.

GMR International Equipment Corporation.

Guardian Fire Equipment, Inc.

Wilson & Cousins Inc.

Standard:  UL 405.

Type:  Exposed, freestanding.

Pressure Rating:  [175 psig (1200 kPa) minimum] [300 psig (2070 kPa)].

Body Material:  Corrosion-resistant metal.

Inlets:  Brass with threads according to NFPA 1963 and matching local fire-department sizes and threads.  Include extension pipe nipples, brass lugged swivel connections, and check devices or clappers.

Caps:  Brass, lugged type, with gasket and chain.

Escutcheon Plate:  Round, brass, floor type.

Outlet:  Bottom, with pipe threads.

Number of Inlets:  [Two] [Three] [Four].

Sleeve:  [Brass] [Not required].

Sleeve Height:  18 inches (460 mm).

Escutcheon Plate Marking:  Similar to "[AUTO SPKR & STANDPIPE] [STANDPIPE]."

Finish[, Including Sleeve]:  [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

Outlet Size:  [NPS 4 (DN 100)] [NPS 5 (DN 125)] [NPS 6 (DN 150)].

ALARM DEVICES

Alarm-device types shall match piping and equipment connections.

Water-Motor-Operated Alarm:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Globe Fire Sprinkler Corporation.

Tyco Fire & Building Products LP.

Victaulic Company.

Viking Corporation.

Standard:  UL 753.

Type:  Mechanically operated, with Pelton wheel.

Alarm Gong:  Cast aluminum with red-enamel factory finish.

Size:  10-inch (250-mm) diameter.

Components:  Shaft length, bearings, and sleeve to suit wall construction.

Inlet:  NPS 3/4 (DN 20).

Outlet:  NPS 1 (DN 25) drain connection.

Electrically Operated Alarm Bell:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Fire-Lite Alarms, Inc.; a Honeywell company.

Notifier; a Honeywell company.

Potter Electric Signal Company.

Standard:  UL 464.

Type:  Vibrating, metal alarm bell.

Size:  [6-inch (150-mm) minimum] [8-inch (200-mm) minimum] [10-inch (250-mm)] diameter.

Finish:  Red-enamel factory finish, suitable for outdoor use.

Water-Flow Indicators:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

ADT Security Services, Inc.

McDonnell & Miller; ITT Industries.

Potter Electric Signal Company.

System Sensor; a Honeywell company.

Viking Corporation.

Watts Industries (Canada) Inc.

Standard:  UL 346.

Water-Flow Detector:  Electrically supervised.

Components:  Two single-pole, double-throw circuit switches for isolated alarm and auxiliary contacts, 7 A, 125-V ac and 0.25 A, 24-V dc; complete with factory-set, field-adjustable retard element to prevent false signals and tamperproof cover that sends signal if removed.

Type:  Paddle operated.

Pressure Rating:  250 psig (1725 kPa).

Design Installation:  Horizontal or vertical.

Pressure Switches:

Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AFAC Inc.

Barksdale, Inc.

Detroit Switch, Inc.

Potter Electric Signal Company.

System Sensor; a Honeywell company.

Tyco Fire & Building Products LP.

United Electric Controls Co.

Viking Corporation.

Standard:  UL 346.

Type:  Electrically supervised water-flow switch with retard feature.

Components:  Single-pole, double-throw switch with normally closed contacts.

Design Operation:  Rising pressure signals water flow.

Valve Supervisory Switches:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Fire-Lite Alarms, Inc.; a Honeywell company.

Kennedy Valve; a division of McWane, Inc.

Potter Electric Signal Company.

System Sensor; a Honeywell company.

Standard:  UL 346.

Type:  Electrically supervised.

Components:  Single-pole, double-throw switch with normally closed contacts.

Design:  Signals that controlled valve is in other than fully open position.

Indicator-Post Supervisory Switches:

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Potter Electric Signal Company.

System Sensor; a Honeywell company.

Standard:  UL 346.

Type:  Electrically supervised.

Components:  Single-pole, double-throw switch with normally closed contacts.

Design:  Signals that controlled indicator-post valve is in other than fully open position.

MANUAL CONTROL STATIONS

Description:  UL listed or FM approved, hydraulic operation, with union, NPS 1/2 (DN 15) pipe nipple, and bronze ball valve.  Include metal enclosure labeled "MANUAL CONTROL STATION" with operating instructions and cover held closed by breakable strut to prevent accidental opening.

CONTROL PANELS

Description:  Single-area, two-area, or single-area cross-zoned control panel as indicated, including NEMA ICS 6, Type 1 enclosure, detector, alarm, and solenoid-valve circuitry for operation of deluge valves.  Panels contain power supply; battery charger; standby batteries; field-wiring terminal strip; electrically supervised solenoid valves and polarized fire-alarm bell; lamp test facility; single-pole, double-throw auxiliary alarm contacts; and rectifier.

Panels:  UL listed and FM approved when used with thermal detectors and Class A detector circuit wiring.  Electrical characteristics are 120-V ac, 60 Hz, with 24-V dc rechargeable batteries.

Manual Control Stations:  Electric operation, metal enclosure, labeled "MANUAL CONTROL STATION" with operating instructions and cover held closed by breakable strut to prevent accidental opening.

Manual Control Stations:  Hydraulic operation, with union, NPS 1/2 (DN 15) pipe nipple, and bronze ball valve.  Include metal enclosure labeled "MANUAL CONTROL STATION" with operating instructions and cover held closed by breakable strut to prevent accidental opening.

PRESSURE GAGES

Manufacturers:  Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AMETEK; U.S. Gauge Division.

Ashcroft Inc.

Brecco Corporation.

WIKA Instrument Corporation.

Standard:  UL 393.

Dial Size:  3-1/2- to 4-1/2-inch (90- to 115-mm) diameter.

Pressure Gage Range:  [0 to 250 psig (0 to 1725 kPa) minimum] [0 to 300 psig (0 to 2070 kPa)].

Water System Piping Gage:  Include "WATER" or "AIR/WATER" label on dial face.

Air System Piping Gage:  Include[ retard feature and] "AIR" or "AIR/WATER" label on dial face.

EXECUTION

PREPARATION

Perform fire-hydrant flow test according to NFPA 14 and NFPA 291.  Use results for system design calculations required in "Quality Assurance" Article.

Report test results promptly and in writing.

EXAMINATION

Examine roughing-in for hose connections and stations to verify actual locations of piping connections before installation.

Examine walls and partitions for suitable thickness, fire- and smoke-rated construction, framing for hose-station cabinets, and other conditions where hose connections and stations are to be installed.

Proceed with installation only after unsatisfactory conditions have been corrected.

SERVICE-ENTRANCE PIPING

Connect fire-suppression standpipe piping to water-service piping at service entrance into building.  Comply with requirements for exterior piping in Section 211100 "Facility Fire-Suppression Water-Service Piping."

Install shutoff valve,[ backflow preventer,] pressure gage, drain, and other accessories at connection to fire-suppression water-service piping.[  Comply with requirements for backflow preventers in Section 211100 "Facility Fire-Suppression Water-Service Piping."]

Install shutoff valve, check valve, pressure gage, and drain at connection to water service.

WATER-SUPPLY CONNECTIONS

Connect fire-suppression standpipe piping to building's interior water-distribution piping.  Comply with requirements for interior piping in Section 221116 "Domestic Water Piping."

Install shutoff valve,[ backflow preventer,] pressure gage, drain, and other accessories at connection to water-distribution piping.[  Comply with requirements for backflow preventers in Section 221119 "Domestic Water Piping Specialties."]

Install shutoff valve, check valve, pressure gage, and drain at connection to water supply.

PIPING INSTALLATION

Locations and Arrangements:  Drawing plans, schematics, and diagrams indicate general location and arrangement of piping.  Install piping as indicated, as far as practical.

Deviations from approved working plans for piping require written approval from authorities having jurisdiction.  File written approval with Architect before deviating from approved working plans.

Piping Standard:  Comply with requirements in NFPA 14 for installation of fire-suppression standpipe piping.

Install seismic restraints on piping.  Comply with requirements in NFPA 13 for seismic-restraint device materials and installation.

Install listed fittings to make changes in direction, branch takeoffs from mains, and reductions in pipe sizes.

Install drain valves on standpipes.  Extend drain piping to outside of building.

Install automatic (ball drip) drain valves to drain piping between fire-department connections and check valves.  Drain to floor drain or outside building.

Install alarm devices in piping systems.

Install hangers and supports for standpipe system piping according to NFPA 14.  Comply with requirements in NFPA 13 for hanger materials.

Install pressure gages on riser or feed main and at top of each standpipe.  Include pressure gages with connection not less than NPS 1/4 (DN 8) and with soft-metal seated globe valve, arranged for draining pipe between gage and valve.  Install gages to permit removal, and install where they will not be subject to freezing.

Drain dry-type standpipe system piping.

Pressurize and check dry-type standpipe system piping and [air-pressure maintenance devices] [air compressors].

Fill wet-type standpipe system piping with water.

Install electric heating cables and pipe insulation on wet-type, fire-suppression standpipe piping in areas subject to freezing.  Comply with requirements for heating cables in Section 210533 "Heat Tracing for Fire-Suppression Piping" and for piping insulation in Section 210700 "Fire-Suppression Systems Insulation."

Connect compressed-air supply to dry-pipe sprinkler piping.

Connect air compressor to the following piping and wiring:

Pressure gages and controls.

Electrical power system.

Fire-alarm devices, including low-pressure alarm.

Install sleeves for piping penetrations of walls, ceilings, and floors.  Comply with requirements for sleeves specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

Install sleeve seals for piping penetrations of concrete walls and slabs.  Comply with requirements for sleeve seals specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

Install escutcheons for piping penetrations of walls, ceilings, and floors.  Comply with requirements for escutcheons specified in Section 210518 "Escutcheons for Fire-Suppression Piping."

JOINT CONSTRUCTION

Install couplings, flanges, flanged fittings, unions, nipples, and transition and special fittings that have finish and pressure ratings same as or higher than system's pressure rating for aboveground applications unless otherwise indicated.

Install unions adjacent to each valve in pipes NPS 2 (DN 50) and smaller.

Install flanges, flange adapters, or couplings for grooved-end piping on valves, apparatus, and equipment having NPS 2-1/2 (DN 65) and larger end connections.

Ream ends of pipes and tubes and remove burrs.  Bevel plain ends of steel pipe.

Remove scale, slag, dirt, and debris from inside and outside of pipes, tubes, and fittings before assembly.

Flanged Joints:  Select appropriate gasket material in size, type, and thickness suitable for water service.  Join flanges with gasket and bolts according to ASME B31.9.

Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

Apply appropriate tape or thread compound to external pipe threads.

Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.

Steel-Piping, Cut-Grooved Joints:  Cut square-edge groove in end of pipe according to AWWA C606.  Assemble coupling with housing, gasket, lubricant, and bolts.  Join steel pipe and grooved-end fittings according to AWWA C606 for steel-pipe joints.

Steel-Piping, Roll-Grooved Joints:  Roll rounded-edge groove in end of pipe according to AWWA C606.  Assemble coupling with housing, gasket, lubricant, and bolts.  Join steel pipe and grooved-end fittings according to AWWA C606 for steel-pipe grooved joints.

Welded Joints:  Construct joints according to AWS D10.12M/D10.12, using qualified processes and welding operators according to "Quality Assurance" Article.

Shop weld pipe joints where welded piping is indicated.  Do not use welded joints for galvanized-steel pipe.

Brazed Joints:  Join copper tube and fittings according to CDA's "Copper Tube Handbook," "Brazed Joints" Chapter.

Copper-Tubing Grooved Joints:  Roll rounded-edge groove in end of tube according to AWWA C606.  Assemble coupling with housing, gasket, lubricant, and bolts.  Join copper tube and grooved-end fittings according to AWWA C606 for steel-pipe grooved joints.

Dissimilar-Material Piping Joints:  Make joints using adapters compatible with materials of both piping systems.

VALVE AND SPECIALTIES INSTALLATION

Install listed fire-protection valves, trim and drain valves, specialty valves and trim, controls, and specialties according to NFPA 14 and authorities having jurisdiction.

Install listed fire-protection shutoff valves supervised-open, located to control sources of water supply except from fire-department connections.  Install permanent identification signs indicating portion of system controlled by each valve.

Install check valve in each water-supply connection.  Install backflow preventers instead of check valves in potable-water-supply sources.

Specialty Valves:

General Requirements:  Install in vertical position for proper direction of flow, in main supply to system.

Alarm Valves:  Install bypass check valve and retarding chamber drain-line connection.

[Dry-Pipe] [and] [Deluge] Valves:  Install trim sets for air supply, drain, priming level, alarm connections, ball drip valves, pressure gages, priming chamber attachment, and fill-line attachment.

Install air compressor and compressed-air supply piping.

Install compressed-air supply piping from building's compressed-air piping system.

HOSE-CONNECTION INSTALLATION

Install hose connections adjacent to standpipes.

Install freestanding hose connections for access and minimum passage restriction.

Install NPS 1-1/2 (DN 40) hose-connection valves with flow-restricting device.

Install NPS 2-1/2 (DN 65) hose connections with quick-disconnect NPS 2-1/2 by NPS 1-1/2 (DN 65 by DN 40) reducer adapter and flow-restricting device.

Install wall-mounted-type hose connections in cabinets.  Include pipe escutcheons, with finish matching valves, inside cabinet where water-supply piping penetrates cabinet.  Install valves at angle required for connection of fire hose.  Comply with requirements for cabinets in Section 104413 "Fire Protection Cabinets."

HOSE-STATION INSTALLATION

Install freestanding hose stations for access and minimum passage restriction.

Install NPS 1-1/2 (DN 40) hose-station valves with flow-restricting device unless otherwise indicated.

Install NPS 2-1/2 (DN 65) hose connections with quick-disconnect NPS 2-1/2 by NPS 1-1/2 (DN 65 by DN 40) reducer adapter and flow-restricting device unless otherwise indicated.

Install freestanding hose stations with support or bracket attached to standpipe.

Install wall-mounted, rack hose stations in cabinets.  Include pipe escutcheons, with finish matching valves, inside cabinet where water-supply piping penetrates cabinet.  Install valves at angle required for connection of fire hose.  Comply with requirements for cabinets in Section 104413 "Fire Protection Cabinets."

Install hose-reel hose stations on wall with bracket.

MONITOR INSTALLATION

Install monitors on standpipe piping.

FIRE-DEPARTMENT CONNECTION INSTALLATION

Install wall-type, fire-department connections.

Install yard-type, fire-department connections in concrete slab support.  Comply with requirements for concrete in Section 033000 "Cast-in-Place Concrete."

Install automatic (ball drip) drain valve at each check valve for fire-department connection.

IDENTIFICATION

Install labeling and pipe markers on equipment and piping according to requirements in NFPA 14.

Identify system components, wiring, cabling, and terminals.  Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

FIELD QUALITY CONTROL

Perform tests and inspections.

Tests and Inspections:

Leak Test:  After installation, charge systems and test for leaks.  Repair leaks and retest until no leaks exist.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Flush, test, and inspect standpipe systems according to NFPA 14, "System Acceptance" Chapter.

Energize circuits to electrical equipment and devices.

Start and run air compressors.

Coordinate with fire-alarm tests.  Operate as required.

Coordinate with fire-pump tests.  Operate as required.

Verify that equipment hose threads are same as local fire-department equipment.

Fire-suppression standpipe system will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

DEMONSTRATION

[Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain specialty valves.

PIPING SCHEDULE

Piping between Fire-Department Connections and Check Valves:  Galvanized, standard-weight steel pipe with [threaded ends; cast-iron threaded fittings; and threaded] [grooved ends; grooved-end fittings; grooved-end-pipe couplings; and grooved] joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [Schedule 30] [or] [thinwall], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [nonstandard OD, thinwall] [or] [hybrid] black-steel pipe with roll-grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Thinwall] [Schedule 10,] [nonstandard OD, thinwall] [or] [hybrid] black-steel pipe with plain ends; welding fittings; and welded joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with plain ends; [cast-] [or] [wrought-]copper solder-joint fittings; and brazed joints.

[Type L (Type B)] [Type M (Type B)], hard copper tube with roll-grooved ends; copper, grooved-end fittings; grooved-end-tube couplings; and grooved joints.

[Standard-weight] [Schedule 30] [or] [thinwall], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [or] [hybrid] black-steel pipe with roll-grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Thinwall] [Schedule 10,] [or] [hybrid] black-steel pipe with plain ends; welding fittings; and welded joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with plain ends; [cast-] [or] [wrought-]copper solder-joint fittings; and brazed joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with roll-grooved ends; copper, grooved-end fittings; grooved-end-tube couplings; and grooved joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [nonstandard OD, thinwall] [or] [hybrid] black-steel pipe with plain ends; welding fittings; and welded joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with [cut] [cut- or roll] [roll]-grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [nonstandard OD, thinwall] [or] [hybrid] black-steel pipe with plain ends; welding fittings; and welded joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Standard-weight] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [nonstandard OD, thinwall] [or] [hybrid] black-steel pipe with plain ends; welding fittings; and welded joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with plain ends; [cast-] [or] [wrought-]copper solder-joint fittings; and brazed joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with roll-grooved ends; copper, grooved-end fittings; grooved-end-tube couplings; and grooved joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Standard-weight] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with plain ends; [cast-] [or] [wrought-]copper solder-joint fittings; and brazed joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with roll-grooved ends; copper, grooved-end fittings; grooved-end-tube couplings; and grooved joints.

END OF SECTION 211200