SECTION 238126 - SPLIT-SYSTEM AIR-CONDITIONERS

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section includes split-system air-conditioning and heat-pump units consisting of separate evaporator-fan and compressor-condenser components.

ACTION SUBMITTALS

Product Data:  For each type of product indicated.  Include rated capacities, operating characteristics, and furnished specialties and accessories.  Include performance data in terms of capacities, outlet velocities, static pressures, sound power characteristics, motor requirements, and electrical characteristics.

LEED Submittals:

Product Data for Credit EA 4:  Documentation indicating that equipment and refrigerants comply.

Shop Drawings:  Include plans, elevations, sections, details, and attachments to other work.

Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Wiring Diagrams:  For power, signal, and control wiring.

INFORMATIONAL SUBMITTALS

Field quality-control reports.

Warranty:  Sample of special warranty.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:  For split-system air-conditioning units to include in emergency, operation, and maintenance manuals.

MAINTENANCE MATERIAL SUBMITTALS

Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Filters:  One set for each air-handling unit.

Gaskets:  One set for each access door.

Fan Belts:  One set for each air-handling unit fan.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in CEC, by a qualified testing agency, and marked for intended location and application.

ASHRAE Compliance:

Fabricate and label refrigeration system to comply with ASHRAE 15, "Safety Standard for Refrigeration Systems."

ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1,  Section 4 - "Outdoor Air Quality," Section 5 - "Systems and Equipment," Section 6 - " Procedures," and Section 7 - "Construction and System Start-up."

ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1.

COORDINATION

Coordinate sizes and locations of concrete bases with actual equipment provided.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork are specified in Section 033000 "Cast-in-Place Concrete."

Coordinate sizes and locations of roof curbs, equipment supports, and roof penetrations with actual equipment provided.

WARRANTY

Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of split-system air-conditioning units that fail in materials or workmanship within specified warranty period.

Warranty Period:

For Compressor: Five year(s) from date of Substantial Completion.

For Parts: One year from date of Substantial Completion.

For Labor: One year from date of Substantial Completion.

PRODUCTS

MANUFACTURERS

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Carrier Corporation; Home Comfort and HVAC Building & Industrial Systems.

Mitsubishi Electric & Electronics USA, Inc.; HVAC Advanced Products Division.

Trane; a business of American Standard companies.

YORK; a Johnson Controls company.

INDOOR UNITS (5 TONS OR LESS)

Concealed Evaporator-Fan Components:

Chassis:  Galvanized steel with flanged edges, removable panels for servicing, and insulation on back of panel.

Insulation:  Faced, glass-fiber duct liner.

Refrigerant Coil:  Copper tube, with mechanically bonded aluminum fins and thermal-expansion valve.  Comply with ARI 206/110.

Fan:  Forward-curved, double-width wheel of galvanized steel; directly connected to motor.

Fan Motors:

Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Multitapped, multispeed with internal thermal protection and permanent lubrication.

Wiring Terminations:  Connect motor to chassis wiring with plug connection.

Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Filters:  Permanent, cleanable.

Condensate Drain Pans:

Fabricated with one percent slope in at least two planes to collect condensate from cooling coils (including coil piping connections, coil headers, and return bends) and humidifiers, and to direct water toward drain connection.

Length:  Extend drain pan downstream from leaving face to comply with ASHRAE 62.1.

Depth:  A minimum of 2 inches deep.

Single-wall, galvanized-steel sheet.

Drain Connection:  Located at lowest point of pan and sized to prevent overflow.  Terminate with threaded nipple on one end of pan.

Minimum Connection Size:  NPS 1.

Pan-Top Surface Coating:  Asphaltic waterproofing compound.

Units with stacked coils shall have an intermediate drain pan to collect condensate from top coil.

Wall-Mounted, Evaporator-Fan Components:

Cabinet:  Enameled steel with removable panels on front and ends in color selected by Architect, and discharge drain pans with drain connection.

Refrigerant Coil:  Copper tube, with mechanically bonded aluminum fins and thermal-expansion valve.  Comply with ARI 206/110.

Fan:  Direct drive, centrifugal.

Fan Motors:

Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Multitapped, multispeed with internal thermal protection and permanent lubrication.

Enclosure Type:  Totally enclosed, fan cooled.

NEMA Premium (TM) efficient motors as defined in NEMA MG 1.

Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in electrical Sections.

Mount unit-mounted disconnect switches on exterior of unit.

Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Filters:  Permanent, cleanable.

Condensate Drain Pans:

Fabricated with one percent slope in at least two planes to collect condensate from cooling coils (including coil piping connections, coil headers, and return bends) and humidifiers, and to direct water toward drain connection.

Length:  Extend drain pan downstream from leaving face to comply with ASHRAE 62.1.

Depth:  A minimum of 1 inch deep.

Single-wall, galvanized-steel sheet.

Drain Connection:  Located at lowest point of pan and sized to prevent overflow.  Terminate with threaded nipple on one end of pan.

Minimum Connection Size:  NPS 1.

Pan-Top Surface Coating:  Asphaltic waterproofing compound.

OUTDOOR UNITS (5 TONS OR LESS)

Air-Cooled, Compressor-Condenser Components:

Casing:  Steel, finished with baked enamel in color selected by Architect, with removable panels for access to controls, weep holes for water drainage, and mounting holes in base.  Provide brass service valves, fittings, and gage ports on exterior of casing.

Compressor:  Hermetically sealed with crankcase heater and mounted on vibration isolation device.  Compressor motor shall have thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

Compressor Type:  Scroll.

Two-speed compressor motor with manual-reset high-pressure switch and automatic-reset low-pressure switch.

Refrigerant Charge: R-410A.

Refrigerant Coil:  Copper tube, with mechanically bonded aluminum fins and liquid subcooler.  Comply with ARI 206/110.

Heat-Pump Components:  Reversing valve and low-temperature-air cutoff thermostat.

Fan:  Aluminum-propeller type, directly connected to motor.

Motor:  Permanently lubricated, with integral thermal-overload protection.

Low Ambient Kit:  Permits operation down to 45 deg F.

Mounting Base:  Polyethylene.

ACCESSORIES

Control equipment and sequence of operation are specified in Section 230900 "Instrumentation and Control for HVAC" and Section 230993 "Sequence and Operations for HVAC Controls."

Thermostat:  Wireless infrared functioning to remotely control compressor and evaporator fan, with the following features:

Compressor time delay.

24-hour time control of system stop and start.

Liquid-crystal display indicating temperature, set-point temperature, time setting, operating mode, and fan speed.

Fan-speed selection including auto setting.

Automatic-reset timer to prevent rapid cycling of compressor.

Refrigerant Line Kits:  Soft-annealed copper suction and liquid lines factory cleaned, dried, pressurized, and sealed; factory-insulated suction line with flared fittings at both ends.

Drain Hose:  For condensate.

Additional Monitoring:

Monitor constant and variable motor loads.

Monitor variable-frequency-drive operation.

Monitor economizer cycle.

Monitor cooling load.

Monitor air distribution static pressure and ventilation air volumes.

EXECUTION

INSTALLATION

Install units level and plumb.

Install evaporator-fan components using manufacturer's standard mounting devices securely fastened to building structure.

Install roof-mounted, compressor-condenser components on equipment supports specified in Section 077200 "Roof Accessories." Anchor units to supports with removable, cadmium-plated fasteners.

Equipment Mounting:

Install ground-mounted, compressor-condenser components on cast-in-place concrete equipment base(s).  Comply with requirements for equipment bases and foundations specified in other sections.

Install ground-mounted, compressor-condenser components on polyethylene mounting base.

Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

Install and connect precharged refrigerant tubing to component's quick-connect fittings.  Install tubing to allow access to unit.

CONNECTIONS

Piping installation requirements are specified in other Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

Where piping is installed adjacent to unit, allow space for service and maintenance of unit.

Duct Connections:  Duct installation requirements are specified in Section 233113 "Metal Ducts." Drawings indicate the general arrangement of ducts.  Connect supply and return ducts to split-system air-conditioning units with flexible duct connectors.  Flexible duct connectors are specified in Section 233300 "Air Duct Accessories."

FIELD QUALITY CONTROL

Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Perform tests and inspections.

Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Tests and Inspections:

Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Remove and replace malfunctioning units and retest as specified above.

Prepare test and inspection reports.

STARTUP SERVICE

Engage a factory-authorized service representative to perform startup service.

Complete installation and startup checks according to manufacturer's written instructions.

DEMONSTRATION

Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain units.

END OF SECTION 238126